## NEW MCC-9 (hidden)
Project Number: | #VALUE!
Date:
Project Name:
LOAD CALCULATION FOR EXISTING SERVICE
CIRCUIT/DESCRIPTION | KW | KVA | HP | FLA
EXISTING LOAD
PEAK DEMAND PER SRP/APS |  | 0 |  | 0
NEW MOTOR LOADS
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
NEW NON-MOTOR LOADS
0
SUBTOTAL |  |  |  | #N/A
+ 25% OF LARGEST MOTOR |  |  |  | #N/A
TOTAL AMPS @ 480V/3PHASE |  |  |  | #N/A
EXISTING SERVICE SIZE (AMPS)
LOAD CALCULATION FOR NEW SERVICE
CIRCUIT/DESCRIPTION | KVA | HP | FLA | VFD? (y or n) | FLA | Breaker Trip Rating | Wire |  | MCC SPACE FACTOR
MOTOR LOADS | [8 empty] | AB Centerline 2100
EAST PRIMARY CLARIFIER 2 |  | 0.5 | 1.1 | n | 1.1 | 3 | 3 #12 W/ #12 GND |  | 1 (12")
WEST PRIMARY CLARIFIER 3 |  | 0.5 | 1.1 | n | 1.1 | 3 | 3 #12 W/ #12 GND |  | 1 (12")
PC SLUDGE PUMP 1 |  | 3 | 4.8 | n | 4.8 | 10 | 3 #12 W/ #12 GND |  | 1 (12")
PC SLUDGE PUMP 2 |  | 5 | 7.6 | n | 7.6 | 15 | 3 #12 W/ #12 GND |  | 1 (12")
PC SCUM PUMP 1 |  | 10 | 14 | n | 14 | 30 | 3 #12 W/ #12 GND |  | 1 (12")
PC SCUM PUMP 2 |  | 10 | * | n | 14 | 30 | 3 #12 W/ #12 GND |  | 1 (12")
SC SCUM PUMP 1 |  | 10 | 14 | n | 14 | 30 | 3 #12 W/ #12 GND |  | 1 (12")
SC SCUM PUMP 2 |  | 10 | * | n | 14 | 30 | 3 #12 W/ #12 GND |  | 1 (12")
AXIAL EFFLUENT PUMP |  | 40 | 52 | y | 52 | 80 | 3 #6 W/ #8 GND |  | 3 (36")
SECONDARY CLARIFIER 1 |  | 1.5 | 3 | n | 3 | 7 | 3 #12 W/ #12 GND |  | 3 (36")
SECONDARY CLARIFIER 2 |  | 1.5 | 3 | n | 3 | 7 | 3 #12 W/ #12 GND |  | 1 (12")
SECONDARY CLARIFIER 3 |  | 1.5 | 3 | n | 3 | 7 | 3 #12 W/ #12 GND |  | 1 (12")
NON-POTABLE WATER PUMP 1 |  | 7.5 | 11 | y | 11 | 15 | 3 #12 W/ #12 GND |  | 3 (36")
NON-POTABLE WATER PUMP 2 |  | 7.5 | 11 | y | 11 | 15 | 3 #12 W/ #12 GND |  | 3 (36")
NON-POTABLE WATER PUMP 3 |  | 7.5 | 11 | y | 11 | 15 | 3 #12 W/ #12 GND |  | 3 (36")
NON-POTABLE WATER PUMP 4 |  | 7.5 | * | y | 11 | 15 | 3 #12 W/ #12 GND |  | 3 (36")
NON-MOTOR LOADS
LIGHTING PANEL TRANSFORMER | 25 |  | 30.106
DIGESTER SUPERNATANT STATION | 25 |  | 30.106
EQUALIZATION POND PANEL | 15 |  | 18.0636
DISTRIBUTION PANEL |  |  | 50
7.5 KW HEATER |  |  | 9
0
SUBTOTAL |  |  | 273.8755
+ 25% OF LARGEST MOTOR |  |  | 13
TOTAL AMPS @ 480V/3PHASE |  |  | 286.8755
SERVICE SIZE (AMPS) |  |  | 300
| Lookup Table | [6 empty] | Conductors |  | Forumulas | 1ø | 3ø | Enter KW | Enter V | Enter PF | Enter ø (1 or 3) | Amps
| Motor HP | NEC FLA | Starter | VFD | Wire Size |  |  | Ampacity | Wire Size | Amps (when KW is known) | KW*1000 V*PF | KW*1000 V*PF*√3
| 0 | 0 | 0 | 0 | 3 #12 W/ #12 GND |  |  | 25 | 3 #12 W/ #12 GND
| 0.5 | 1.1 | 3 | 15 | 3 #12 W/ #12 GND |  |  | 30 | 3 #10 W/ #10 GND | Amps (when KVA is known) | KVA*1000 V | KVA*1000 V*√3 |  |  | NA
| 0.75 | 1.6 | 3 | 15 | 3 #12 W/ #12 GND |  |  | 40 | 3 #8 W/ #10 GND
| 1 | 2.1 | 3 | 15 | 3 #12 W/ #12 GND |  |  | 55 | 3 #6 W/ #10 GND
| 1.5 | 3 | 7 | 15 | 3 #12 W/ #12 GND |  |  | 70 | 3 #4 W/ #8 GND
| 2 | 3.4 | 7 | 15 | 3 #12 W/ #12 GND |  |  | 100 | 3 #3 W/ #8 GND
| 3 | 4.8 | 10 | 15 | 3 #12 W/ #12 GND |  |  | 115 | 3 #2 W/ #6 GND
| 5 | 7.6 | 15 | 15 | 3 #12 W/ #12 GND |  |  | 130 | 3 #1 W/ #6 GND
| 7.5 | 11 | 20 | 15 | 3 #12 W/ #12 GND |  |  | 150 | 3 1/0 W/ #6 GND
| 10 | 14 | 30 | 20 | 3 #12 W/ #12 GND |  |  | 175 | 3 2/0 W/ #6 GND
| 15 | 21 | 40 | 30 | 3 #10 W/ #10 GND |  |  | 200 | 3 3/0 W/ #6 GND
| 20 | 27 | 50 | 40 | 3 #10 W/ #10 GND |  |  | 230 | 3 4/0 W/ #4 GND
| 25 | 34 | 50 | 50 | 3 #8 W/ #10 GND |  |  | 255 | 3 250 MCM W/ #4 GND
| 30 | 40 | 70 | 60 | 3 #8 W/ #10 GND |  |  | 285 | 3 250 MCM W/ #4 GND
| 40 | 52 | 100 | 80 | 3 #6 W/ #8 GND |  |  | 310 | 3 350 MCM W/ #3 GND
| 50 | 65 | 150 | 100 | 3 #4 W/ #8 GND |  |  | 335 | 3 400 MCM W/ #3 GND
| 60 | 77 | 200 | 125 | 3 #3 W/ #8 GND |  |  | 380 | 3 500 MCM W/ #3 GND
| 75 | 96 | 200 | 150 | 3 #1 W/ #6 GND |  |  | 400 | 2 PR 3 3/0 W/ #6 GND
| 100 | 124 | 200 | 200 | 3 2/0 W/ #6 GND |  |  | 500 | 2 PR 3 3/0 W/ #6 GND
| 125 | 156 | 250 | 250 | 3 3/0 W/ #6 GND |  |  | 600 | 2 PR 3 250 MCM W/ #4 GND
| 150 | 180 | 300 | 300 | 3 4/0 W/ #4 GND |  |  | 800 | 3 PR 3 300 MCM W/ #4 GND
| 200 | 240 | 400 | 400 | 3 350 MCM W/ #3 GND |  |  | 1000 | 3 PR 3 400 MCM W/ #3 GND
| 250 | 302 | 500 | 500 | 3 500 MCM W/ #3 GND |  |  | 1200 | 4 PR 3 350 MCM W/ #3 GND
| 300 | 361 | 600 | 600 | 2 PR 3 4/0 W/ #4 GND |  |  | 1600 | 5 PR 3 400 MCM W/ #3 GND
| 350 | 414 | 700 | 700 | 2 PR 3 300 MCM W/ #4 GND
| 400 | 477 | 800 | 800 | 2 PR 3 350 MCM W/ #3 GND
| 450 | 515 | 900 | 900 | 2 PR 3 400 MCM W/ #3 GND
| 500 | 590 | 1000 | 1000 | 2 PR 3 500 MCM W/ #3 GND

## EXISTING MCC-9 (hidden)
Project Number: | #VALUE!
Date:
Project Name:
LOAD CALCULATION FOR EXISTING SERVICE
CIRCUIT/DESCRIPTION | KW | KVA | HP | FLA
EXISTING LOAD
PEAK DEMAND PER SRP/APS |  | 0 |  | 0
NEW MOTOR LOADS
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
NEW NON-MOTOR LOADS
0
SUBTOTAL |  |  |  | #N/A
+ 25% OF LARGEST MOTOR |  |  |  | #N/A
TOTAL AMPS @ 480V/3PHASE |  |  |  | #N/A
EXISTING SERVICE SIZE (AMPS)
LOAD CALCULATION FOR NEW SERVICE
CIRCUIT/DESCRIPTION | KVA | HP | FLA | VFD? (y or n) | FLA | Breaker Trip Rating | Wire
MOTOR LOADS
SLUDGE PUMP 3 |  | 5 | 7.6 | n | 7.6 | 15 | 3 #12 W/ #12 GND
FERRIC PUMP 3 (FUTURE) |  | 15 | 21 | n | 21 | 40 | 3 #10 W/ #10 GND
EAST PRIMARY CLARIFIER 2 |  | 0.5 | 1.1 | n | 1.1 | 3 | 3 #12 W/ #12 GND
WEST PRIMARY CLARIFIER 3 |  | 0.5 | 1.1 | n | 1.1 | 3 | 3 #12 W/ #12 GND
FERRIC PUMP 4 |  | 15 | 21 | n | 21 | 40 | 3 #10 W/ #10 GND
FINAL CLARIFIER 1 |  | 0.5 | 1.1 | n | 1.1 | 3 | 3 #12 W/ #12 GND
SLUDGE PUMP 1 |  | 3 | 4.8 | n | 4.8 | 10 | 3 #12 W/ #12 GND
FILTER FEED PUMP 1 |  | 15 | 21 | n | 21 | 40 | 3 #10 W/ #10 GND
SLUDGE PUMP 3 |  | 5 | 7.6 | n | 7.6 | 15 | 3 #12 W/ #12 GND
SLUDGE PUMP 2 |  | 5 | 7.6 | n | 7.6 | 15 | 3 #12 W/ #12 GND
FILTER FEED PUMP 2 |  | 15 | 21 | n | 21 | 40 | 3 #10 W/ #10 GND
SLUDGE PUMP 4 |  | 3 | 4.8 | n | 4.8 | 10 | 3 #12 W/ #12 GND
RECIRC PUMP 2 |  | 10 | 14 | n | 14 | 30 | 3 #12 W/ #12 GND
FILTER FEED PUMP 3 |  | 15 | 21 | n | 21 | 40 | 3 #10 W/ #10 GND
RECIRC PUMP 1 |  | 10 | 14 | n | 14 | 30 | 3 #12 W/ #12 GND
FIXED FILM REACTOR FEED PUMP 1 |  | 25 | 34 | n | 34 | 50 | 3 #8 W/ #10 GND
FIXED FILM REACTOR FEED PUMP 2 |  | 25 | 34 | n | 34 | 50 | 3 #8 W/ #10 GND
FIXED FILM REACTOR FEED PUMP 3 |  | 25 | 34 | n | 34 | 50 | 3 #8 W/ #10 GND
NON-MOTOR LOADS
PANEL LLP9 TRANSFORMER | 25 |  | 30.106
PLC CONTROL PANEL TRANSFORMER | 1 |  | 1.2042
DIGESTER SUPERNATANT STATION |  |  | 0
EQUALIZATION POND PANEL |  |  | 0
PANEL HP9 |  |  | 0
MCC-9A |  |  | 83.3
0
SUBTOTAL |  |  | 300.806
+ 25% OF LARGEST MOTOR |  |  | 8.5
TOTAL AMPS @ 480V/3PHASE |  |  | 309.306
SERVICE SIZE (AMPS) |  |  | 600
| Lookup Table | [6 empty] | Conductors |  | Forumulas | 1ø | 3ø | Enter KW | Enter V | Enter PF | Enter ø (1 or 3) | Amps
| Motor HP | NEC FLA | Starter | VFD | Wire Size |  |  | Ampacity | Wire Size | Amps (when KW is known) | KW*1000 V*PF | KW*1000 V*PF*√3
| 0 | 0 | 0 | 0 | 3 #12 W/ #12 GND |  |  | 25 | 3 #12 W/ #12 GND
| 0.5 | 1.1 | 3 | 15 | 3 #12 W/ #12 GND |  |  | 30 | 3 #10 W/ #10 GND | Amps (when KVA is known) | KVA*1000 V | KVA*1000 V*√3 |  |  | NA
| 0.75 | 1.6 | 3 | 15 | 3 #12 W/ #12 GND |  |  | 40 | 3 #8 W/ #10 GND
| 1 | 2.1 | 3 | 15 | 3 #12 W/ #12 GND |  |  | 55 | 3 #6 W/ #10 GND
| 1.5 | 3 | 7 | 15 | 3 #12 W/ #12 GND |  |  | 70 | 3 #4 W/ #8 GND
| 2 | 3.4 | 7 | 15 | 3 #12 W/ #12 GND |  |  | 100 | 3 #3 W/ #8 GND
| 3 | 4.8 | 10 | 15 | 3 #12 W/ #12 GND |  |  | 115 | 3 #2 W/ #6 GND
| 5 | 7.6 | 15 | 15 | 3 #12 W/ #12 GND |  |  | 130 | 3 #1 W/ #6 GND
| 7.5 | 11 | 20 | 15 | 3 #12 W/ #12 GND |  |  | 150 | 3 1/0 W/ #6 GND
| 10 | 14 | 30 | 20 | 3 #12 W/ #12 GND |  |  | 175 | 3 2/0 W/ #6 GND
| 15 | 21 | 40 | 30 | 3 #10 W/ #10 GND |  |  | 200 | 3 3/0 W/ #6 GND
| 20 | 27 | 50 | 40 | 3 #10 W/ #10 GND |  |  | 230 | 3 4/0 W/ #4 GND
| 25 | 34 | 50 | 50 | 3 #8 W/ #10 GND |  |  | 255 | 3 250 MCM W/ #4 GND
| 30 | 40 | 70 | 60 | 3 #8 W/ #10 GND |  |  | 285 | 3 250 MCM W/ #4 GND
| 40 | 52 | 100 | 80 | 3 #6 W/ #8 GND |  |  | 310 | 3 350 MCM W/ #3 GND
| 50 | 65 | 150 | 100 | 3 #4 W/ #8 GND |  |  | 335 | 3 400 MCM W/ #3 GND
| 60 | 77 | 200 | 125 | 3 #3 W/ #8 GND |  |  | 380 | 3 500 MCM W/ #3 GND
| 75 | 96 | 200 | 150 | 3 #1 W/ #6 GND |  |  | 400 | 2 PR 3 3/0 W/ #6 GND
| 100 | 124 | 200 | 200 | 3 2/0 W/ #6 GND |  |  | 500 | 2 PR 3 3/0 W/ #6 GND
| 125 | 156 | 250 | 250 | 3 3/0 W/ #6 GND |  |  | 600 | 2 PR 3 250 MCM W/ #4 GND
| 150 | 180 | 300 | 300 | 3 4/0 W/ #4 GND |  |  | 800 | 3 PR 3 300 MCM W/ #4 GND
| 200 | 240 | 400 | 400 | 3 350 MCM W/ #3 GND |  |  | 1000 | 3 PR 3 400 MCM W/ #3 GND
| 250 | 302 | 500 | 500 | 3 500 MCM W/ #3 GND |  |  | 1200 | 4 PR 3 350 MCM W/ #3 GND
| 300 | 361 | 600 | 600 | 2 PR 3 4/0 W/ #4 GND |  |  | 1600 | 5 PR 3 400 MCM W/ #3 GND
| 350 | 414 | 700 | 700 | 2 PR 3 300 MCM W/ #4 GND
| 400 | 477 | 800 | 800 | 2 PR 3 350 MCM W/ #3 GND
| 450 | 515 | 900 | 900 | 2 PR 3 400 MCM W/ #3 GND
| 500 | 590 | 1000 | 1000 | 2 PR 3 500 MCM W/ #3 GND

## EXISTING MCC-9A (hidden)
Project Number: | #VALUE!
Date:
Project Name:
LOAD CALCULATION FOR EXISTING SERVICE
CIRCUIT/DESCRIPTION | KW | KVA | HP | FLA
EXISTING LOAD
PEAK DEMAND PER SRP/APS |  | 0 |  | 0
NEW MOTOR LOADS
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
|  |  |  | #N/A | #N/A
NEW NON-MOTOR LOADS
0
SUBTOTAL |  |  |  | #N/A
+ 25% OF LARGEST MOTOR |  |  |  | #N/A
TOTAL AMPS @ 480V/3PHASE |  |  |  | #N/A
EXISTING SERVICE SIZE (AMPS)
LOAD CALCULATION FOR NEW SERVICE
CIRCUIT/DESCRIPTION | KVA | HP | FLA | VFD? (y or n) | FLA | Breaker Trip Rating | Wire
MOTOR LOADS
PC SCUM PUMP 1 |  | 10 | 14 | n | 14 | 30 | 3 #12 W/ #12 GND
PC SCUM PUMP 2 |  | 10 | 14 | n | 14 | 30 | 3 #12 W/ #12 GND
AXIAL EFFLUENT PUMP |  | 40 | 52 | n | 52 | 100 | 3 #6 W/ #8 GND
PCE-WG1 |  | 0.5 | 1.1 | n | 1.1 | 3 | 3 #12 W/ #12 GND
PCE-BV2 |  | 0.5 | 1.1 | n | 1.1 | 3 | 3 #12 W/ #12 GND
PCE-BV3 |  | 0.5 | 1.1 | n | 1.1 | 3 | 3 #12 W/ #12 GND
NON-MOTOR LOADS
PANEL HP9A |  |  | 0
0
0
0
0
0
0
SUBTOTAL |  |  | 83.3
+ 25% OF LARGEST MOTOR |  |  | 13
TOTAL AMPS @ 480V/3PHASE |  |  | 96.3
SERVICE SIZE (AMPS) |  |  | 600
| Lookup Table | [6 empty] | Conductors |  | Forumulas | 1ø | 3ø | Enter KW | Enter V | Enter PF | Enter ø (1 or 3) | Amps
| Motor HP | NEC FLA | Starter | VFD | Wire Size |  |  | Ampacity | Wire Size | Amps (when KW is known) | KW*1000 V*PF | KW*1000 V*PF*√3
| 0 | 0 | 0 | 0 | 3 #12 W/ #12 GND |  |  | 25 | 3 #12 W/ #12 GND
| 0.5 | 1.1 | 3 | 15 | 3 #12 W/ #12 GND |  |  | 30 | 3 #10 W/ #10 GND | Amps (when KVA is known) | KVA*1000 V | KVA*1000 V*√3 |  |  | NA
| 0.75 | 1.6 | 3 | 15 | 3 #12 W/ #12 GND |  |  | 40 | 3 #8 W/ #10 GND
| 1 | 2.1 | 3 | 15 | 3 #12 W/ #12 GND |  |  | 55 | 3 #6 W/ #10 GND
| 1.5 | 3 | 7 | 15 | 3 #12 W/ #12 GND |  |  | 70 | 3 #4 W/ #8 GND
| 2 | 3.4 | 7 | 15 | 3 #12 W/ #12 GND |  |  | 100 | 3 #3 W/ #8 GND
| 3 | 4.8 | 10 | 15 | 3 #12 W/ #12 GND |  |  | 115 | 3 #2 W/ #6 GND
| 5 | 7.6 | 15 | 15 | 3 #12 W/ #12 GND |  |  | 130 | 3 #1 W/ #6 GND
| 7.5 | 11 | 20 | 15 | 3 #12 W/ #12 GND |  |  | 150 | 3 1/0 W/ #6 GND
| 10 | 14 | 30 | 20 | 3 #12 W/ #12 GND |  |  | 175 | 3 2/0 W/ #6 GND
| 15 | 21 | 40 | 30 | 3 #10 W/ #10 GND |  |  | 200 | 3 3/0 W/ #6 GND
| 20 | 27 | 50 | 40 | 3 #10 W/ #10 GND |  |  | 230 | 3 4/0 W/ #4 GND
| 25 | 34 | 50 | 50 | 3 #8 W/ #10 GND |  |  | 255 | 3 250 MCM W/ #4 GND
| 30 | 40 | 70 | 60 | 3 #8 W/ #10 GND |  |  | 285 | 3 250 MCM W/ #4 GND
| 40 | 52 | 100 | 80 | 3 #6 W/ #8 GND |  |  | 310 | 3 350 MCM W/ #3 GND
| 50 | 65 | 150 | 100 | 3 #4 W/ #8 GND |  |  | 335 | 3 400 MCM W/ #3 GND
| 60 | 77 | 200 | 125 | 3 #3 W/ #8 GND |  |  | 380 | 3 500 MCM W/ #3 GND
| 75 | 96 | 200 | 150 | 3 #1 W/ #6 GND |  |  | 400 | 2 PR 3 3/0 W/ #6 GND
| 100 | 124 | 200 | 200 | 3 2/0 W/ #6 GND |  |  | 500 | 2 PR 3 3/0 W/ #6 GND
| 125 | 156 | 250 | 250 | 3 3/0 W/ #6 GND |  |  | 600 | 2 PR 3 250 MCM W/ #4 GND
| 150 | 180 | 300 | 300 | 3 4/0 W/ #4 GND |  |  | 800 | 3 PR 3 300 MCM W/ #4 GND
| 200 | 240 | 400 | 400 | 3 350 MCM W/ #3 GND |  |  | 1000 | 3 PR 3 400 MCM W/ #3 GND
| 250 | 302 | 500 | 500 | 3 500 MCM W/ #3 GND |  |  | 1200 | 4 PR 3 350 MCM W/ #3 GND
| 300 | 361 | 600 | 600 | 2 PR 3 4/0 W/ #4 GND |  |  | 1600 | 5 PR 3 400 MCM W/ #3 GND
| 350 | 414 | 700 | 700 | 2 PR 3 300 MCM W/ #4 GND
| 400 | 477 | 800 | 800 | 2 PR 3 350 MCM W/ #3 GND
| 450 | 515 | 900 | 900 | 2 PR 3 400 MCM W/ #3 GND
| 500 | 590 | 1000 | 1000 | 2 PR 3 500 MCM W/ #3 GND

## MCC-EBH (7) (hidden)
Project Number: | #VALUE!
Date:
Project Name:
LOAD CALCULATION FOR EXISTING SERVICE
CIRCUIT/DESCRIPTION | KW | KVA | HP | FLA
EXISTING LOAD
NEW MOTOR LOADS
#N/A
EXISTING NON-MOTOR LOADS
SUBTOTAL |  |  |  | 0
+ 25% OF LARGEST MOTOR |  |  |  | 0
TOTAL AMPS @ 480V/3PHASE |  |  |  | 0
EXISTING SERVICE SIZE (AMPS) |  |  |  | 150
LOAD CALCULATION FOR NEW SERVICE
CIRCUIT/DESCRIPTION | KVA | HP | FLA | VFD? (y or n) | FLA | Breaker Trip Rating | Wire
MCC-EBH MOTOR LOADS
STORM DRAIN PUMP 1 (23-P-2100) |  | 5 | 7.6 | n | 7.6 | 15 | 3 #12 W/ #12 GND
STORM DRAIN PUMP 2 (23-P-2200) |  | 5 | 7.6 | n | 7.6 | 15 | 3 #12 W/ #12 GND
STORM DRAIN PUMP 3 (23-P-2300) |  | 5 | 7.6 | n | 7.6 | 15 | 3 #12 W/ #12 GND
NON-POTABLE WATER PUMP 1 (81-P-1100) |  | 10 | 14 | Y | 14 | 20 | 3 #12 W/ #12 GND
NON-POTABLE WATER PUMP 2 (81-P-1200) |  | 10 | 14 | Y | 14 | 20 | 3 #12 W/ #12 GND
NON-POTABLE WATER PUMP 3 (81-P-1300) |  | 10 | 14 | Y | 14 | 20 | 3 #12 W/ #12 GND
NON-POTABLE WATER PUMP 4 (81-P-1400) |  | 10 | * | Y | 14 | 20 | 3 #12 W/ #12 GND
STORAGE BUILDING EXHUAST FAN (97-H-1100) |  | 0.75 | 1.6 | n | 1.6 | 3 | 3 #12 W/ #12 GND
NON-MOTOR LOADS
LIGHTING PANEL | 10 |  | 12.0424
MCP-CB |  |  | 30
SUBTOTAL |  |  | 108.4424
+ 25% OF LARGEST MOTOR |  |  | 3.5
TOTAL AMPS @ 480V/3PHASE |  |  | 111.9424
SERVICE SIZE (AMPS) |  |  | 150
55.75
| Lookup Table | [6 empty] | Conductors |  | Forumulas | 1ø | 3ø | Enter KW | Enter V | Enter PF | Enter ø (1 or 3) | Amps
| Motor HP | NEC FLA | Starter | VFD | Wire Size |  |  | Ampacity | Wire Size | Amps (when KW is known) | KW*1000 V*PF | KW*1000 V*PF*√3
| 0 | 0 | 0 | 0 | 3 #12 W/ #12 GND |  |  | 25 | 3 #12 W/ #12 GND
| 0.5 | 1.1 | 3 | 15 | 3 #12 W/ #12 GND |  |  | 30 | 3 #10 W/ #10 GND | Amps (when KVA is known) | KVA*1000 V | KVA*1000 V*√3 |  |  | NA
| 0.75 | 1.6 | 3 | 15 | 3 #12 W/ #12 GND |  |  | 40 | 3 #8 W/ #10 GND
| 1 | 2.1 | 3 | 15 | 3 #12 W/ #12 GND |  |  | 55 | 3 #6 W/ #10 GND
| 1.5 | 3 | 7 | 15 | 3 #12 W/ #12 GND |  |  | 70 | 3 #4 W/ #8 GND
| 2 | 3.4 | 7 | 15 | 3 #12 W/ #12 GND |  |  | 100 | 3 #3 W/ #8 GND
| 3 | 4.8 | 10 | 15 | 3 #12 W/ #12 GND |  |  | 115 | 3 #2 W/ #6 GND
| 5 | 7.6 | 15 | 15 | 3 #12 W/ #12 GND |  |  | 130 | 3 #1 W/ #6 GND
| 7.5 | 11 | 20 | 15 | 3 #12 W/ #12 GND |  |  | 150 | 3 1/0 W/ #6 GND
| 10 | 14 | 30 | 20 | 3 #12 W/ #12 GND |  |  | 175 | 3 2/0 W/ #6 GND
| 15 | 21 | 40 | 30 | 3 #10 W/ #10 GND |  |  | 200 | 3 3/0 W/ #6 GND
| 20 | 27 | 50 | 40 | 3 #10 W/ #10 GND |  |  | 230 | 3 4/0 W/ #4 GND
| 25 | 34 | 50 | 50 | 3 #8 W/ #10 GND |  |  | 255 | 3 250 MCM W/ #4 GND
| 30 | 40 | 70 | 60 | 3 #8 W/ #10 GND |  |  | 285 | 3 250 MCM W/ #4 GND
| 40 | 52 | 100 | 80 | 3 #6 W/ #8 GND |  |  | 310 | 3 350 MCM W/ #3 GND
| 50 | 65 | 150 | 100 | 3 #4 W/ #8 GND |  |  | 335 | 3 400 MCM W/ #3 GND
| 60 | 77 | 200 | 125 | 3 #3 W/ #8 GND |  |  | 380 | 3 500 MCM W/ #3 GND
| 75 | 96 | 200 | 150 | 3 #1 W/ #6 GND |  |  | 400 | 2 PR 3 3/0 W/ #6 GND
| 100 | 124 | 200 | 200 | 3 2/0 W/ #6 GND |  |  | 500 | 2 PR 3 3/0 W/ #6 GND
| 125 | 156 | 250 | 250 | 3 3/0 W/ #6 GND |  |  | 600 | 2 PR 3 250 MCM W/ #4 GND
| 150 | 180 | 300 | 300 | 3 4/0 W/ #4 GND |  |  | 800 | 3 PR 3 300 MCM W/ #4 GND
| 200 | 240 | 400 | 400 | 3 350 MCM W/ #3 GND |  |  | 1000 | 3 PR 3 400 MCM W/ #3 GND
| 250 | 302 | 500 | 500 | 3 500 MCM W/ #3 GND |  |  | 1200 | 4 PR 3 350 MCM W/ #3 GND
| 300 | 361 | 600 | 600 | 2 PR 3 4/0 W/ #4 GND |  |  | 1600 | 5 PR 3 400 MCM W/ #3 GND
| 350 | 414 | 700 | 700 | 2 PR 3 300 MCM W/ #4 GND
| 400 | 477 | 800 | 800 | 2 PR 3 350 MCM W/ #3 GND
| 450 | 515 | 900 | 900 | 2 PR 3 400 MCM W/ #3 GND
| 500 | 590 | 1000 | 1000 | 2 PR 3 500 MCM W/ #3 GND

## LP-UV-2
Project Number:
Date:
Project Name:
PANEL: | LP-UV-2 | VOLTAGE: | 120/240 | MAIN CB: | 200 AMP | BUS AMPS: | 225 AMP
CB TYPE: | BOLT-ON | MOUNTING: | SURFACE | BUS BRACING: | 22KA | BKR AIC: | 22KA
CIRCUIT DESCRIPTION | BKR | CIRCUIT | LINE 1 | LINE 2 | CIRCUIT | BKR | CIRCUIT DESCRIPTION
BIOASSAY LAB LIGHTS (6, A) | 20/1 | 1 | 258
|  |  | 29 |  | 2 | 20/1 | UV BUILDING MECH ROOM LIGHT (1, C)
UV BUILDING OUTSIDE LIGHTS (5, F) | 20/1 | 3 |  | 200
|  |  |  | 63 | 4 | 20/1 | UV BUILDING BATHROOM LIGHT & FAN (B)
UV BUILDING PROCESS AREA LIGHTS (14, D) | 20/1 | 5 | 896
|  |  | 12 |  | 6 | 20/1 | UV BUILDING EXIT LIGHTS (5, G)
UV BUILDING ELECTRICAL ROOM LIGHTS (4, E) | 20/1 | 7 |  | 172
|  |  |  | 540 | 8 | 20/1 | BIOASSAY LAB OUTLETS (3, H)
BIOASSAY LAB OUTLETS (3, I) | 20/1 | 9 | 540
|  |  | 360 |  | 10 | 20/1 | BIOASSAY LAB OUTLETS (2, J)
BIOASSAY REFRIGERATOR OUTLET | 20/1 | 11 |  | 540
|  |  |  | 540 | 12 | 20/1 | UV BUILDING PROCESS AREA OUTLETS (3, L)
UV BLDG BATHROOM & MECH OUTLETS (2, K) | 20/1 | 13 | 360
|  |  | 100 |  | 14 | 20/1 | LIGHTING CONTROL PANEL (LCP-UV)
UV BUILDING PROCESS AREA OUTLETS (2, M) | 20/1 | 15 |  | 360
|  |  |  | 500 | 16 | 20/1 | UV BUILDING GARAGE DOOR
UV BLDG ELECTRICAL ROOM OUTLETS (4, N) | 20/1 | 17 | 720
|  |  | 1000 |  | 18 | 30/2 | GENERATOR HEATER
PLC-UV | 20/1 | 19 |  | 500
|  |  |  | 1000 | 20
SINK WATER HEATER | 20/1 | 21 | 1440
|  |  | 1200 |  | 22 | 20/1 | 43-P-1500
43-P-1400 | 20/1 | 23 |  | 1200
|  |  |  | 500 | 24 | 20/1 | GENERATOR CHARGER
SPARE | 20/1 | 25 | 0
|  |  | 500 |  | 26 | 20/1 | 43-AIT-1650
43-AIT-1660 | 20/1 | 27 |  | 500
|  |  |  | 1000 | 28 | 20/1 | GARAGE DOOR
FUTURE 51-FIT-1005 | 20/1 | 29
|  |  | 0 |  | 30 | 20/1 | SPARE
SPARE | 20/1 | 31 |  | 0
|  |  |  | 0 | 32 | 20/1 | SPARE
SPARE | 20/1 | 33 | 0
|  |  | 0 |  | 34 | 20/1 | SPARE
MCP-UV | 20/1 | 35 |  | 500
|  |  |  | 0 | 36 | 20/1 | SPARE
SPARE | 20/1 | 37 | 0
[5 empty] | 38 | 20/1
SPARE | 20/1 | 39 |  | 0
[5 empty] | 40 | 20/1
230V WALL OUTLET | 30/2 | 41 | 1500
[5 empty] | 42 | 20/1
|  | 43 |  | 1500
|  |  |  | 1800 | 44 | 40/2 | WATER HEATER BREAKER 1
WATER HEATER BREAKER 2 | 40/2 | 45 | 1800
|  |  | 1800 |  | 46
|  | 47 |  | 1800
|  |  |  | 1800 | 48 | 40/2 | WATER HEATER BREAKER 3
SAMPLE PUMP BY UV CHANNELS (4, R) | 20/1 | 49 | 1000
|  |  | 1800 |  | 50
SAMPLE PUMP RECEPTACLES IN BIOASSAY (2, O) | 20/1 | 51 |  | 1000
|  |  |  | 0 | 52 | 20/2 | SPARE
DECHLOR PUMP (44-P-1900) AND ANALYZERS RECEPTICLES (2, P) | 20/1 | 53 | 1000
|  |  | 0 |  | 54
SPARE | 20/1 | 55 |  | 0
|  |  |  | 180 | 56 | 20/2 | SITE LIGHTING 1 (3 LIGHTS)
SITE LIGHTING 2 (4 LIGHTS) | 20/2 | 57 | 240
|  |  | 180 |  | 58
|  | 59 |  | 240
|  |  |  | 0 | 60 | 20/1 | SPARE
51-M-1009 VAULT SUMP PUMP | 20/1 | 61 | 1500
[5 empty] | 62 | 20/1 | SPARE
SPARE | 20/1 | 63
[5 empty] | 64 | 20/1 | SPARE
SPARE | 20/1 | 65
[6 empty] | 20/1 | SPARE
SPARE | 20/1 | 67 |  |  | 66
[6 empty] | 20/1 | SPARE
SPARE | 20/1 | 69 |  |  | 68
[6 empty] | 20/1 | SPARE
SPARE | 20/1 | 71 |  |  | 70
[6 empty] | 20/1 | SPARE
CONNECTED VA PER PHASE |  |  | 18235 | 16435 | NOTES:
CONNECTED AMPS PER PHASE |  |  | 151.9583 | 136.9583
25% OF CONTINUOUS & LIGHTING LOAD (VA) |  |  | 528.75 | 338.75
LARGEST MOTOR (25%) |  |  | 375 | 0
CODE VA PER PHASE |  |  | 19138.75 | 16773.75
CODE AMPS PER PHASE |  |  | 159.4896 | 139.7812

## Existing LP-RW
Project Number: | #VALUE! | [7 empty] | Standard Circuit Counts:
Date:
Project Name: | [8 empty] | 30
42
54
72
PANEL: | LP-RW | VOLTAGE: | 120/208 | MAIN CB: | 200 AMP | BUS AMPS: | 200 AMP
CB TYPE: | BOLT-ON | MOUNTING: | SURFACE | BUS A.I.C: | 10KA | BKR AIC: | 10KA
CIRCUIT DESCRIPTION | BKR | CIRCUIT | PHASE A | PHASE B | PHASE C | CIRCUIT | BKR | CIRCUIT DESCRIPTION
MAIN FLOOR LIGHTS (10, A) | 20/1 | 1 | 490
|  |  | 392 |  |  | 2 | 20/1 | MAIN FLOOR LIGHTS (8, B)
MAIN FLOOR LIGHTS (8, C) | 20/1 | 3 |  | 392
|  |  |  | 120 |  | 4 | 20/1 | OUTDOOR LIGHTS (2, E)
MAIN FLOOR LIGHTS (10, D) | 20/1 | 5 |  |  | 490
[5 empty] | 120 | 6 | 20/1 | OUTDOOR LIGHTS (2, F)
MAIN FLOOR RECEPTACLES (3, G) | 20/1 | 7 | 540
|  |  | 540 |  |  | 8 | 20/1 | MAIN FLOOR RECEPTACLES (3, H)
MAIN FLOOR RECEPTACLES (3, I) | 20/1 | 9 |  | 540
|  |  |  | 539 |  | 10 | 20/1 | MEZZANINE LIGHTS (11, J)
MEZZANINE LIGHTS (12, K) | 20/1 | 11 |  |  | 588
[5 empty] | 540 | 12 | 20/1 | MEZZANINE RECEPTACLES (3, L)
MEZZANINE RECEPTACLES (3, M) | 20/1 | 13 | 540
|  |  | 147 |  |  | 14 | 20/1 | ELECTRICAL ROOM LIGHTS (3, N)
ELECTRICAL ROOM RECEPTACLES (2, O) | 20/1 | 15 |  | 360
|  |  |  | 360 |  | 16 | 20/1 | OUTDOOR RECEPTACLES (2, P)
EMERGENCY LIGHTS (3, Q) | 20/1 | 17 |  |  | 9.6
[5 empty] | 1176 | 18 | 20/1 | AC-M-4 AIR DRYER
MBH-AC-1 | 20/1 | 19 | 56
|  |  | 56 |  |  | 20 | 20/1 | MBH-AC-4
SPARE | 20/1 | 21
|  |  |  | 1176 |  | 22 | 20/1 | CI-P-1 METERING PUMP
LCP-52-1001 | 20/1 | 23 |  |  | 300
[5 empty] | 1200 | 24 | 20/1 | MB1-M-1 PROCESS SKID 1
MB2-M-1 PROCESS SKID 2 | 20/1 | 25 | 1200
|  |  | 1200 |  |  | 26 | 20/1 | MB3-M-1 PROCESS SKID 3
PLC-RW | 20/1 | 27 |  | 100
|  |  |  | 100 |  | 28 | 20/1 | MBH-D-1 DAMPER
MB4-M-1 PROCESS SKID 4 | 20/1 | 29 |  |  | 1200
[5 empty] | 100 | 30 | 20/1 | MBH-D-2 DAMPER
MBH-EF-1 EXHAUST FAN | 20/1 | 31 | 1176
|  |  | 100 |  |  | 32 | 20/1 | MBH-D-3 DAMPER
MBH-EF-2 EXHAUST FAN | 20/1 | 33 |  | 1176
|  |  |  | 100 |  | 34 | 20/1 | MBH-D-4 DAMPER
MBH-EF-3 EXHAUST FAN | 20/1 | 35 |  |  | 1176
[5 empty] | 500 | 36 | 20/1 | ROLL-UP DOOR OPENERS(2,R)
MBH-AC-2 | 30/2 | 37 | 2600
|  |  | 200 |  |  | 38 | 20/1 | CTC-RW
|  | 39 |  | 2600
|  |  |  | 2600 |  | 40 | 30/2 | MBH-AC-5
MBH-T-1 | 20/1 | 41 |  |  | 100
[5 empty] | 2600 | 42
MBH-T-2 | 20/1 | 43 | 100
|  |  | 1200 |  |  | 44 | 20/1 | MF3-M-1 PROCESS SKID 3
MF4-M-1 PROCESS SKID 4 | 20/1 | 45 |  | 1200
|  |  |  | 50 |  | 46 | 20/1 | 52-AIT-1200
FLOC TANK LEAK DETECTOR | 20/1 | 47 |  |  | 100
[5 empty] | 500 | 48 | 20/1 | 52-AIT-1250
SPARE | 20/1 | 49
|  |  | 1800 |  |  | 50 | 100/3 | LP-UV
SPARE | 20/1 | 51
|  |  |  | 1000 |  | 52
SPARE | 20/1 | 53
[5 empty] | 881 | 54
CONNECTED VA PER PHASE |  |  | 12337 | 12413 | 11580.6 | NOTES:
CONNECTED AMPS PER PHASE |  |  | 102.8083 | 103.4417 | 96.505
25% OF CONTINUOUS & LIGHTING LOAD (VA) |  |  | 172.5 | 98 | 122.5
LARGEST MOTOR (25%) |  |  | 122.5 | 98 | 122.5
CODE VA PER PHASE |  |  | 12632 | 12609 | 11825.6
CODE AMPS PER PHASE |  |  | 105.2667 | 105.075 | 98.5467

## LP-AB
Project Number:
Date: | [8 empty] | PI-10 | 31-AIT-2010
Project Name: | [9 empty] | 31-AIT-1010
31-AIT-1001
31-AIT-2001
PANEL: | LP-AB | VOLTAGE: | 120/240 | MAIN CB: | 225 AMP | BUS AMPS: | 225 AMP |  | PI-11 | 23-FIT-1010
CB TYPE: | BOLT-ON | MOUNTING: | SURFACE | BUS BRACING: | 22KA | BKR AIC: | 22KA |  |  | 23-FIT-1020
CIRCUIT DESCRIPTION | BKR | CIRCUIT | LINE 1 | LINE 2 | CIRCUIT | BKR | CIRCUIT DESCRIPTION |  |  | 31-AIT-4010
ELECTRICAL BLDG. LIGHTS (8, A) | 20/1 | 1 | 288 | [6 empty] | 31-AIT-3001
|  |  | 80 |  | 2 | 20/1 | ELECTRICAL BLDG. OUTDOOR LIGHTS (2, B) |  |  | 31-AIT-4001
ELECTRICAL BLDG. OUTLETS (3, C) | 20/1 | 3 |  | 540
|  |  |  | 100 | 4 | 20/1 | LIGHTING CONTROL PANEL (LCP-AB) |  | PI-12 | 36-FIT-1000
CTC-AB | 20/1 | 5 | 1000
|  |  | 816 |  | 6 | 20/1 | EQ/ANOXIC BASINS LIGHTS/OUTLETS (4,3) |  | PI-13 | 44-FIT-1000
AEROTOR BASINS LIGHTS/OUTLETS (4,3) | 20/1 | 7 |  | 816 | [5 empty] | FLOW VAULT SUMP
|  |  |  | 500 | 8 | 20/1 | 43-P-1100
AEROTOR BASINS LIGHTS/OUTLETS (4,3) | 20/1 | 9 | 816 | [5 empty] | PI-16 | 51-FIT-1009
|  |  | 0 |  | 10 | 20/1 | 43-P-1200 | X |  | 81-FIT-1001
PLC-AB | 20/1 | 11 |  | 500 |  |  |  | X
|  |  |  | 100 | 12 | 20/1 | 43-AIT-1620 | X | PI-26 | 52-AIT-1250 | Chlorine analyzers
43-AIT-1630 | 20/1 | 13 | 100 |  |  |  |  | X |  | 52-AIT-1260 | not marked with voltage
|  |  | 100 |  | 14 | 20/1 | 23-FIT-1010 | X |  | 44-AIT-1940 | need 120vac right?
51-FIT-1009 | 20/1 | 15 |  | 100 |  |  |  | X |  | 44-P-1900
|  |  |  | 1500 | 16 | 20/1 | POND RETURN SUMP | X |  | 44-FIT-1920
23-FIT-1020 | 20/1 | 17 | 100 |  |  |  |  | X
|  |  | 100 |  | 18 | 20/1 | 31-AIT-1010 | X
44-FIT-1000 | 20/1 | 19 |  | 100 |  |  |  | X
|  |  |  | 100 | 20 | 20/1 | 31-AIT-4010 | X
31-AIT-2010 | 20/1 | 21 | 100 |  |  |  |  | X
|  |  | 100 |  | 22 | 20/1 | 31-AIT-2001 | X
31-AIT-1001 | 20/1 | 23 |  | 100 |  |  |  | X
|  |  |  | 100 | 24 | 20/1 | 31-AIT-4001 | X
DECLOR HEAT TRACE | 20/1 | 25 | 1600
|  |  | 100 |  | 26 | 20/1 | 43-AIT-1600 | X
31-AIT-3001 | 20/1 | 27 |  | 100 |  |  |  | X
|  |  |  | 100 | 28 | 20/1 | 43-AIT-1610 | X
36-FIT-1000 | 20/1 | 29 | 100 |  |  |  |  | X
|  |  | 100 |  | 30 | 20/1 | 42-FIT-1120 | X
SC 1 LIGHTS AND OUTLET | 20/1 | 31 |  | 318 |  |  |  | X
|  |  |  | 567 | 32 | 20/1 | SC 2 LIGHTS AND OUTLET | X
SC 3 LIGHTS AND OUTLET (FUTURE) | 20/1 | 33 | 318 |  |  |  |  | X
|  |  | 240 |  | 34 | 20/1 | 31-H-1110
31-H-1210 | 20/1 | 35 |  | 240
|  |  |  | 400 | 36 | 20/1 | EXISTING 21-LIT-1101, 21-LIT-1204B, 21-LIT-1304B, 21-LIT-1305B | X
EXISTING 21-LIT-1204A, 21-LIT-1205A, 21-LIT-1304A, 21-LIT-1305A | 20/1 | 37 | 400 |  |  |  |  | X
|  |  | 100 |  | 38 | 20/1 | EXISTING 51-LIT-1101 | X
EXISTING SITE LIGHTING L1, L2, L3, L4, L5, L6, L8, L9 | 20/2 | 39 |  | 350 |  |  |  | X
|  |  |  | 100 | 40 | 20/1 | 43-LIT-1010 | X
|  | 41 | 350 |  |  |  |  | X
|  |  | 100 |  | 42 | 20/1 | 43-LIT-1020 | X
61-LIT-1000 | 20/1 | 43 |  | 100 |  |  |  | X
|  |  |  | 100 | 44 | 20/1 | 23-LIT-1002 | X
MCC-AB2 LOW LEVEL RELAY SECTION (MCC-AB2 SECTION 12) | 20/1 | 45 | 100 |  |  |  |  | X
|  |  | 100 |  | 46 | 20/1 | MCC-AB3 LOW LEVEL RELAY SECTION (MCC-AB3 SECTION 12) | X
FUTURE EQ BASIN CHEM PUMP AND ANALYZER | 20/1 | 47 |  | 1000 |  |  |  | X
|  |  |  | 360 | 48 | 20/1 | LOCAL YARD RECEPTACLES
FUTURE METHANOL PUMP EAST OF ANOXIC BASIN 3 | 20/1 | 49 | 1000 |  |  |  |  | X
|  |  | 360 |  | 50 | 20/1 | RECEPTACLE AT CONSOLES
CHLORINATION STRUCTURE EXHAUST/LIGHTS | 20/1 | 51 |  | 200
|  |  |  | 100 | 52 | 20/1 | 36-FIT-1000
EXISTING EFFLUENT PIT LIGHTING | 20/1 | 53 | 200
|  |  | 1000 |  | 54 | 20/2 | DECLOR HEATER
EXISTING EFFLUENT PIT RECEPTACLE | 20/1 | 55 |  | 600
|  |  |  | 1000 | 56 | 20/2
SUMP RECEPTCLE (42-P-1120) | 20/1 | 57 | 1500
|  |  | 1500 |  | 58 | 20/1 | SAMPLING PUMP
SAMPLING PUMP | 20/1 | 59 |  | 1500
|  |  |  | 18 | 60 | 20/1 | UV DISINFECTION DAMPER 1 (44-H-1611)
SAMPLING PUMP | 20/1 | 61 | 1500
|  |  | 18 |  | 62 | 20/1 | UV DISINFECTION DAMPER 2 (44-H-1621)
43-P-1300 | 20/1 | 63
|  |  |  | 18 | 64 | 20/1 | UV DISINFECTION DAMPER 3 (44-H-1631)
43-AIT-1340 | 20/1 | 65
[5 empty] | 66 | 20/1 | SPARE
SPARE | 20/1 | 67
[5 empty] | 68 | 20/1 | SPARE
SPARE | 20/1 | 69
[5 empty] | 70 | 20/1 | SPARE
SPARE | 20/1 | 71
[5 empty] | 72 | 20/1 | SPARE
CONNECTED VA PER PHASE |  |  | 14286 | 11727 | NOTES:
CONNECTED AMPS PER PHASE |  |  | 119.05 | 97.725
25% OF CONTINUOUS & LIGHTING LOAD (VA) |  |  | 887.5 | 741.5
LARGEST MOTOR (25%) |  |  | 375 | 250
CODE VA PER PHASE |  |  | 15548.5 | 12718.5
CODE AMPS PER PHASE |  |  | 129.5708 | 105.9875

## LP-MCC3
Project Number:
Date:
Project Name:
PANEL: | LP-RWDP | VOLTAGE: | 120/240 | MAIN CB: | 100 AMP | BUS AMPS: | 100 AMP
CB TYPE: | BOLT-ON | MOUNTING: | SURFACE | BUS BRACING: | 22KA | BKR AIC: | 22KA
CIRCUIT DESCRIPTION | BKR | CIRCUIT | LINE 1 | LINE 2 | CIRCUIT | BKR | CIRCUIT DESCRIPTION
62-FIT-2620 | 20/1 | 1 | 100
|  |  | 500 |  | 2 | 20/1 | OUTLETS AT THICKENER
THICKENER LIGHTS | 20/1 | 3 |  | 240
|  |  |  | 220 | 4 | 20/1 | LIGHTS
PLC-MCC3 | 20/1 | 5 | 500
|  |  | 380 |  | 6 | 20/1 | OUTLETS
OUTDOOR LIGHTS | 20/1 | 7 |  | 220
[5 empty] | 8 | 20/1 | SPARE
SPARE | 20/1 | 9
[5 empty] | 10 | 20/1 | SPARE
SPARE | 20/1 | 11
[5 empty] | 12 | 20/1 | SPARE
SPARE | 20/1 | 13
[5 empty] | 14 | 20/1 | SPARE
SPARE | 20/1 | 15
[5 empty] | 16 | 20/1 | SPARE
CONNECTED VA PER PHASE |  |  | 1480 | 680 | NOTES:
CONNECTED AMPS PER PHASE |  |  | 12.3333 | 5.6667
25% OF CONTINUOUS & LIGHTING LOAD (VA) |  |  | 370 | 170
LARGEST MOTOR (25%) |  |  | 0 | 0
CODE VA PER PHASE |  |  | 1850 | 850
CODE AMPS PER PHASE |  |  | 15.4167 | 7.0833

## LP-RWDP
Project Number:
Date:
Project Name:
PANEL: | LP-RWDP | VOLTAGE: | 120/240 | MAIN CB: | 225 AMP | BUS AMPS: | 225 AMP
CB TYPE: | BOLT-ON | MOUNTING: | SURFACE | BUS BRACING: | 22KA | BKR AIC: | 22KA
CIRCUIT DESCRIPTION | BKR | CIRCUIT | LINE 1 | LINE 2 | CIRCUIT | BKR | CIRCUIT DESCRIPTION
51-FIT-1006 | 20/1 | 1 | 100
|  |  | 1000 |  | 2 | 20/1 | 120VAC OUTLET AT MMWD TANK
51-FIT-1007 | 20/1 | 3 |  | 100
|  |  |  | 1000 | 4 | 20/1 | 240VAC OUTLET AT MMWD TANK
CTC-RWDP | 20/1 | 5 | 500
|  |  | 1000 |  | 6 | 20/1
OUTLETS | 20/1 | 7 |  | 500
|  |  |  | 100 | 8 | 20/1 | 52-AIT-1260
SITE LIGHTS | 20/1 | 9 | 230
|  |  | 500 |  | 10 | 20/1 | CTC-MMWD
SPARE | 20/1 | 11 |  | 0
|  |  |  | 0 | 12 | 20/1 | SPARE
SPARE | 20/1 | 13 | 0
|  |  | 0 |  | 14 | 20/1 | SPARE
SPARE | 20/1 | 15 |  | 0
|  |  |  | 0 | 16 | 20/1 | SPARE
CONNECTED VA PER PHASE |  |  | 3330 | 1700 | NOTES:
CONNECTED AMPS PER PHASE |  |  | 27.75 | 14.1667
25% OF CONTINUOUS & LIGHTING LOAD (VA) |  |  | 832.5 | 425
LARGEST MOTOR (25%) |  |  | 0 | 0
CODE VA PER PHASE |  |  | 4162.5 | 2125
CODE AMPS PER PHASE |  |  | 34.6875 | 17.7083